## wfbfeas3
"WoodFuelBoilerFinancialFeasibility" - a personal computer spreadsheet program for preliminary financial feasibility analysis of wood fueled steam boiler systems.
This program was designed to provide preliminary financial feasibility analysis in the consideration of using wood or bark fuel as a replacement or alternative to other boiler fuels in space heating or process heat systems.
This program is designed to be suitable for use in preliminary analyses ONLY and is in no way a substitute for technical systems analyses and planning by an engineering professional.
In final business plans, this program can serve as a companion to, but is not intended to be a substitute for, suitable pro-forma financial statements prepared by an accounting professional.
This spreadsheet program was developed by Bob Govett with the support of Lumberjack RC&D, the Wisconsin DNR and the USDA US Forest Service.
The support and assistance of Terry Mace of the WI DNR, Scott Bowe UW-Madison, and John Dramm, Lew McCreery, Richard Bergman and John Zerbe of the USFS in development and review of this program is gratefully acknowledged.
The special technical assistance in engineering review and information regarding boiler costing provided by Al Andersen, the A.L. Andersen Companies Inc, PO Box 26, Waunakee, WI 53597 phone 608-849-7400 is also gratefully acknowledged.
A key concept in the design of this program, is to permit users having very limited subject knowledge to be able use the program to perform very basic initial assessments including simple "PAYBACK" estimations, to ascertain if further study is warranted.
More advanced elements of the program go beyond simple "PAYBACK" analysis and permit persons with appropriate knowledge and expertise to be able to continue with more detailed follow-on preliminary assessments.
This spreadsheet is designed to provide a simple and relatively "friendly" model for preliminary analyses. Use of this spreadsheet for significant or important analyses (beyond preliminary feasibility analysis) should only be done by experienced users.
Within the initial design and continued development of this model, an underlying objective has always been to allow easy ease of use for both experienced and less-experienced users, and to permit easy changes and modification.
Much more robust (and complicated) models exist for more very detailed analysis of biomass projects from aspects of economics, design and environmental aspects - an excellent example is the Canadian RETScreen International Biomass Heating Project Model.
Modification of this spreadsheet in any fashion should only be undertaken by someone with superior knowledge of topic, the program logic, and spreadsheet programming.
This version of the spreadsheet includes advanced modifications completed in June 2004.
FIRST TIME USERS - It is MOST STRONGLY suggested that you carefully read explanatory text related to entries, calculations and interpretations.
For assistance in using this spreadsheet contact:
Bob Govett, College of Natural Resources, University of Wisconsin-Stevens Point, Stevens Point WI 54481
contact information: phone: 715-346-4212; email: rgovett@uwsp.edu; FAX: 715-346-4821
Note: The data entered in this example is a hypothetical representation of replacement of a gas fired boiler with a wood fired boiler - to be fired with purchased fuel - load is dry kilns approximately 200 MBF capacity - the existing boiler needs replacement but is suitable as a backup, the choice in this example is regarding replacement with a new gas-fired boiler, or with a new wood-fired boiler, considered as an incremental investment.
PRELIMINARY ECONOMIC ANALYSIS OF A WOOD OR BARK FUELED BOILER SYSTEM - INITIAL ASSESSMENT
Within the initial assessment section - on rows which are not in bold text and where the code "e>" is shown in column A, an entry is to be made in column C.
This may be ignored for fuels that are not considered as current or alternate to wood fuel in the analysis being conducted.
Entry numbers in the rows are included - these are for illustrative purposes, and in many cases provide a good initial estimate for many values.
These entry numbers, should provide a good initial estimate - and in many cases are amplified to the right - these should be checked and changed if appropriate.
The entry numbers in the rows for the per input unit FUEL COST must be checked and changed if appropriate to your circumstance.
IF the cost per net MILLION Btu of the current (or alternate) fuel is known you can proceed directly to that input at the bottom of this section.
Assuming the cost per net MILLION Btu of the current fuel is unknown OR if you would like to check your calculations or assumptions......
then you should first start with doing an estimate of the cost per net MILLION Btu of your current fuel.
To do this, at a minimum, you will need to know the delivered cost per input unit (gallon, ton, MCF, etc) of the current fuel.
This delivered cost, assumptions regarding gross Btu/input unit for the fuel and boiler efficiency will be combined in the estimation.
NOTE: The assumed gross Btu per unit and assumed efficiency should be reasonable assumptions for each fuel, but......
those data can (and should) be modified if you have better information regarding your circumstance.
Absent better information, the assumptions (except fuel cost) should be reasonable for at least an initial assessment in preliminary analysis.
PRELIMINARY ECONOMIC ANALYSIS - INITIAL ASSESSMENT - ESTIMATION OF FUEL COSTS PER MILLION Btu CURRENT (or alternate) FUEL
to calculate for #2 fuel oil
e> | What is the cost per gallon for this fuel? | 1.31
e> | What is the assumed MILLION gross Btu per gallon? | 0.1388 | .138 to .143 should be a reasonable estimate for this fuel - modify this entry if you have better data for your fuel
e> | What is the assumed net boiler efficiency in %? | 82.5% | .80 to .83 should be a reasonable estimate for a typical system using this fuel - modify this entry if you have better data for your system
| Calculated cost per net MILLION Btu of #2 fuel oil is: | 11.44
to calculate for #6 fuel oil
e> | What is the cost per gallon for this fuel? | 1.41
e> | What is the assumed MILLION gross Btu per gallon? | 0.15 | this should be a reasonable estimate for this fuel - modify this entry if you have better data for your fuel
e> | What is the assumed net boiler efficiency in %? | 82.5% | .80 to .83 should be a reasonable estimate for a typical system using this fuel - modify this entry if you have better data for your system
| Calculated cost per net MILLION Btu of #6 fuel oil is: | 11.3939
to calculate for kerosene
e> | What is the cost per gallon for this fuel? | 1.41
e> | What is the assumed MILLION gross Btu per gallon? | 0.131 | this should be a reasonable estimate for this fuel - modify this entry if you have better data for your fuel
e> | What is the assumed net boiler efficiency in %? | 80% | this should be a reasonable estimate for a typical system using this fuel - modify this entry if you have better data for your system
| Calculated cost per net MILLION Btu of kerosene is: | 13.4542
to calculate for propane purchased on a per gallon basis
e> | What is the cost per gallon for this fuel? | 1.24
e> | What is the assumed MILLION gross Btu per gallon? | 0.0913 | this should be a reasonable estimate for this fuel - modify this entry if you have better data for your fuel
e> | What is the assumed net boiler efficiency in %? | 78.7% | 78% to 79% should be a reasonable estimate for a typical system using this fuel - modify this entry if you have better data for your system
| Calculated cost per net MILLION Btu of propane (gallon basis) is: | 17.2574
to calculate for propane purchased on a per MCF basis
e> | What is the cost per thousand cubic feet for this fuel? | 34.36
e> | What is the assumed MILLION gross Btu per 1,000 ft3? | 2.53 | this should be a reasonable estimate for this fuel - modify this entry if you have better data for your fuel
e> | What is the assumed net boiler efficiency in %? | 78.7% | 78% to 79% should be a reasonable estimate for a typical system using this fuel - modify this entry if you have better data for your system
| Calculated cost per net MILLION Btu of propane (MCF basis) is: | 17.2567
to calculate for natural gas
e> | What is the cost per therm (or "CCF") for this fuel? | 0.68288 | Note: a "therm" (often abbreviated CCF short for 100 cubic feet) is accepted to represent 100,000 Btu - a "Decatherm" is approximately 1,000 cubic feet or approximately 1 million Btu
e> | What is the assumed MILLION gross Btu per therm? | 0.1 | a therm is accepted to represent 100,000 Btu and should be a reasonable estimate for this fuel - modify this entry if you have better data for your fuel
e> | What is the assumed net boiler efficiency in %? | 80% | this should be a reasonable estimate for a typical system using this fuel - modify this entry if you have better data for your system
| Calculated cost per net MILLION Btu of natural gas is: | 8.536
to calculate for anthracite or bituminous coal (higher grade coal)
e> | What is the cost per ton for this fuel? | 75 | bituminous (soft) coal includes low volatile (about 28.7 Million Btu/ton) and high volatile (about 24.7 Million Btu/ton), anthracite (hard coal) is (about 26.3 Million Btu/ton)
e> | What is the assumed MILLION gross Btu per ton? | 26.3 | between 24.7 and 28.7 should be a reasonable estimate for this fuel - modify this entry if you have better data for your fuel
e> | What is the assumed net boiler efficiency in %? | 85% | 75% to 85% should be a reasonable estimate for a typical system using this fuel - modify this entry if you have better data for your system
| Calculated cost per net MILLION Btu of bituminous coal is: | 3.355
to calculate for lignite or subbituminous coal (lower grades of coal)
e> | What is the cost per ton for this fuel? | 60 | subbituminous (soft) coal is a lower grade of coal than bituminous (about 19.2 Million Btu/ton) but of a higher grade than lignite which is also called "brown coal" (about 13.9 Million Btu/ton)
e> | What is the assumed MILLION gross Btu per ton? | 19.2 | this should be a reasonable estimate for this fuel (lignite is much lower, about 13.9) - modify this entry if you have better data for your fuel
e> | What is the assumed net boiler efficiency in %? | 75% | 75% to 80% should be a reasonable estimate for a typical system using this fuel - modify this entry if you have better data for your system
| Calculated cost per net MILLION Btu of subbituminous coal is: | 4.1667
to calculate for electricity
e> | What is the cost per kWh for this fuel? | 0.06879
e> | What is the assumed MILLION gross Btu per kWh? | 0.003412 | this should be a reasonable estimate for this fuel - modify this entry if you have better data for your fuel
e> | What is the assumed net boiler efficiency in %? | 98% | this should be a reasonable estimate for a typical system using this fuel - modify this entry if you have better data for your system
| Calculated cost per net MILLION Btu of electricity is: | 20.5726
to calculate for wood pellets
e> | What is the cost per ton for this fuel? | 70
e> | What is the assumed MILLION gross Btu per ton? | 16 | between 16.0 and 18.0 should be a reasonable estimate for this fuel - modify this entry if you have better data for your fuel
e> | What is the assumed net boiler efficiency in %? | 79% | 78% to 80% should be a reasonable estimate for a typical system using this fuel - modify this entry if you have better data for your system
| Calculated cost per net MILLION Btu of wood pellets is: | 5.538
to calculate for firewood (stove type system)
e> | What is the cost per dry cord for this fuel? | 90
e> | What is the assumed MILLION gross Btu per cord? | 17 | between 15 and 28 million gross Btu per approximate 128 ft3 dry cord is a reasonable estimate for this fuel - modify this entry if you have better data for your fuel
e> | What is the assumed net stove system efficiency in %? | 50% | stove system efficiencies vary widely - this should be a reasonable estimate for a typical system using this fuel - modify this entry if you have better data for your system
| Calculated cost per net MILLION Btu of firewood is: | 10.5882
SUMMARY - Calculated cost per net MILLION Btu of current fuel (from your input assumptions above)
| Calculated cost per net MILLION Btu of #2 fuel oil is: | 11.44
| Calculated cost per net MILLION Btu of #6 fuel oil is: | 11.3939
| Calculated cost per net MILLION Btu of kerosene is: | 13.4542
| Calculated cost per net MILLION Btu of propane (gallon basis) is: | 17.2574
| Calculated cost per net MILLION Btu of propane (MCF basis) is: | 17.2567
| Calculated cost per net MILLION Btu of natural gas is: | 8.536
| Calculated cost per net MILLION Btu of bituminous coal is: | 3.355
| Calculated cost per net MILLION Btu of subbituminous coal is: | 4.1667
| Calculated cost per net MILLION Btu of electricity is: | 20.5726
| Calculated cost per net MILLION Btu of wood pellets is: | 5.538
| Calculated cost per net MILLION Btu of firewood is: | 10.5882
(note: These calculated cost values (above) are relevant ONLY if you have checked or entered the relevant information regarding your circumstances.
The example numbers which were initially in the spreadsheet are simply illustrations that may be significantly different than your circumstances.
PRELIMINARY ECONOMIC ANALYSIS - INITIAL ASSESSMENT - ESTIMATION OF FUEL COSTS PER YEAR, and
COMPARISON OF CURRENT (or alternate) FUEL WITH WOOD OR BARK FUELED BOILER SYSTEM
To conduct the comparison of current (or alternate) boiler system with a wood or bark fueled boiler system.....
a logical starting point is to begin with an estimation of average annual fuel costs for each system.
To do this, the following information is required for each system:
required information for the analysis is:
| the cost per net MILLION Btu of fuel | * this may be calculated if not known
| MILLION Btu (net) required per Day | * this may be estimated if other basic data and annual fuel cost is known
| assumed number of days the boiler is used per year | * this should be known or can be readily assumed
to calculate for current (or alternate) system if above data are known:
e> | What is the cost per net MILLION Btu of current fuel? | 8.5
e> | How many MILLION Btu (net) are required per Day? | 60
| Calculated Average Fuel Cost per day of boiler operation | 510
e> | Assumed # days boiler is used per year (for analysis) is? | 365
| Calculated Average Fuel Cost per Year - current system | 186150
to calculate for current system if:
the MILLION Btu (net) required per Day is NOT known......
BUT the Average Fuel Cost per Year with the current system IS known
e> | What is the average Fuel Cost per Year - current system | 186150
e> | Assumed # days boiler is used per year (for analysis) is? | 365
| Calculated Average Fuel Cost per day of boiler operation | 510
e> | What is the cost per net MILLION Btu of current fuel? | 8.5
| Calculated number of MILLION Btu (net) required per Day? | 60
THE ABOVE ROWS HAVE BEEN USED FOR BASIC CALCULATIONS AND ESTIMATIONS
YOU SHOULD NOW BE READY TO ENTER THE DATA FOR COMPARISON OF THE TWO SYSTEMS
FOR THE CURRENT SYSTEM (OR ALTERNATIVE TO WOOD-BARK FUELED SYSTEM)
e> | What is the cost per net MILLION Btu of current fuel? | 8.5
e> | How many MILLION Btu (net) are required per Day? | 60
| Calculated Average Fuel Cost per day of boiler operation | 510
e> | Assumed # days boiler is used per year (for analysis) is? | 365
| Calculated MILLION Btu (net) that are required per YEAR | 21900
| Calculated Average Fuel Cost per Year - current system | 186150
FOR THE WOOD/BARK FUELED SYSTEM
to calculate for wood or bark fueled boiler system
e> | What is the delivered cost per green ton for this fuel? | 27.5
e> | What is the green basis moisture content for this fuel as delivered? | 35% | a green basis MC indicates what percentage of the total weight (of wood + water in the wood) is water - see note #1 below
| Calculated ovendry basis moisture content for this fuel is: | 53.85% | a ovendry basis MC is expressing the total moisture (water in wood) as a percentage of the weight of ovendry wood - see note #2 below
e> | What is the assumed heat of combustion (HHV) in Btu per dry pound of wood or bark? | 8250 | The value for heat of combustion (HHV or Higher heating value) expressed in Btu per dry pound - see note #3 below
| Calculated fuel value in Btu/lb at moisture content for this fuel is: | 4950 | the calculated fuel value for heat of combustion at the moisture content of the fuel - see note #4
| Calculated as the assumed MILLION gross Btu per green ton of fuel: | 9.9 | this calculation should be a reasonable estimate for this fuel based on the data you have entered r.e. Btu/dry pound and % moisture.
e> | What is the assumed net boiler efficiency in %? | 80% | this should be a reasonable estimate for a typical system using this fuel - modify this entry if you have better data for your system
| Calculated cost per net MILLION Btu of wood or bark boiler system is: | 3.4722
e> | What is the estimated additional annual (non-fuel) operating cost for the wood system? | 20000 | see note #5 below:
e> | What is the fraction of annual Btu needs to be supplied by the wood system %? | 95% | this would be 100% if no backup system is used
| Calculated MILLION Btu (net) to be supplied from the wood system per YEAR is: | 20805
| Calculated MILLION Btu (net) from the wood system per operational day is: | 57
| Calculated fuel cost per YEAR for the wood or bark boiler system is: | 72239.5833
| Calculated annual Btu needs to be supplied by a backup system %? | 5%
| Calculated MILLION Btu (net) supplied from the backup system per YEAR | 1095
e> | What is the cost per net MILLION Btu of fuel for the backup boiler system? | 8.5
| Calculated fuel cost per YEAR for the backup boiler system is: | 9307.5
| Calculated average TOTAL fuel cost per YEAR for the wood system is: | 81547.0833 | note: this includes both wood/bark fuel and backup boiler fuel
Note #1: A green basis moisture content expresses the percentage of the total weight (of wood plus water in the wood) that is water - this varies WIDELY with species, if the wood has dried after harvest, etc.
Generally about 44% to 45% MC on a green basis is a reasonable estimate for many hardwoods, some dense hardwoods are lower. Many softwoods and low density hardwoods such as aspen can exceed 50% - modify this entry if you have better data for your fuel.
Note #2: Ovendry basis moisture content expresses the total moisture (water in wood) as a percentage of the weight of ovendry wood - the ovendry basis MC % frequently will exceed 100% (this simply means the water in green wood weighs more than the dry wood.
The ovendry basis MC varies WIDELY with species, and also within species (e.g. if the wood has dried after harvest, etc.) - an ovendry about 80% is a reasonable estimate for many hardwoods, many softwoods and hardwoods such as aspen can exceed 100%.
Many chip and residual suppliers know the moisture content of the material they sell. Average MC values for various species are contained in many reference texts including the USDA-FS Wood Handbook.
Note #3: The value for heat of combustion varies based on type of fuel this ranges typically from about 8,000 to 8,500 Btu/lb in non-resinous woods such as hardwoods, and from about 8,500 to 9,500 Btu/lb for resinous woods such as pines.
In most but not all cases, HHVs are somewhat higher for bark, ranging from about 7,500 up to 9,500 Btu/lb for non-resinous bark and from about 8,500 up to about 10,500 Btu/lb for resinous bark.
In many cases, good estimates may be found in published data such as USDA-FS General Technical Report FPL 29 and various other reference sources. Fuel sources may also be tested in a laboratory to determine this value.
Note #4: The calculated fuel value for heat of combustion at the moisture content of the fuel is less than the published heat of combustion (or HHV) and it is also less than simply a percentage reduction associated with moisture in the fuel.
In addition to reduction of available potential heat due to moisture in fuel, a further reduction is necessary to accounts for stack gas heat loss due to moisture and other factors.
Note #5: Wood or bark fueled boiler systems frequently cost more to operate on a variable cost basis other than fuel. At a minimum there is typically additional labor cost associated with operating a wood boiler system for fueling, ash removal, etc.
If there was a SAVINGS in operational costs with the wood system this may be reflected as a negative number (i.e. a negative cost)
PRELIMINARY ECONOMIC ANALYSIS - INITIAL ASSESSMENT - ESTIMATION OF AVERAGE ANNUAL FUEL COST SAVINGS WITH WOOD OR BARK FUELED BOILER SYSTEM
| Calculated potential annual savings considering fuel cost differences ONLY | 104602.9167 | note: this DOES NOT include any other costs/saving associated with the wood system
| Calculated potential NET annual savings considering BOTH fuel and operational costs: | 84602.9167 | note: This would typically reflect a net of annual cost reduction associated with fuel cost of wood fuel and an increased cost of operation associated with wood fuel
IMPORTANT NOTE!!!!!!!!!
If the calculated potential NET annual savings considering fuel and operational costs above is a negative OR a very small number....
AND - Assuming you are reasonably confident of your assumptions............
Then it probably does not make sense to spend considerable resources in further analysis at this time.
If your circumstances change significantly you may wish to investigate this again at a later date.
HOWEVER........
IF the calculated potential NET annual savings considering fuel and operational costs is significant to you....
Assuming you are reasonably confident of your assumptions, then at a minimum some simple payback estimates are warranted:
PRELIMINARY ECONOMIC ANALYSIS - INITIAL ASSESSMENT - SIMPLIFIED PAYBACK ESTIMATION FOR WOOD OR BARK FUELED BOILER SYSTEM
ESTIMATIONS REGARDING REQUIREMENTS FOR THE WOOD/BARK FUELED SYSTEM
| to do some simplified payback estimates for the wood or bark fueled boiler system |  |  |  | GREEN | DRY
|  |  |  | Boiler | Wood/Bark | Wood/Bark
| START WITH AN ESTIMATE OF WOOD SYSTEM BOILER HORSEPOWER |  |  | Size | FUEL | FUEL
| Calculated MILLION Btu (net) from the wood system per operational day is: | 57 |  | 50 HP | 182500 | 175000
| Calculated average MILLION Btu per operational hour is: | 2.375 |  | 100 HP | 237500 | 225000
| Calculated wood system boiler horsepower to achieve AVERAGE Btu requirements is: | 70.9379 |  | 150 HP | 395000 | 370000
| Note: The assumed system horsepower should exceed calculated average requirement: |  |  | 200 HP | 555000 | 515000
e> | Assumed wood system boiler horsepower is? | 150 |  | 250 HP | 675000 | 625000
| Calculated peak capacity percentage greater than average requirements is: | 111.5% |  | 300 HP | 745000 | 685000
| Note: For use during periods of high demand the % above is what is available beyond "average" |  |  | 350 HP | 810000 | 745000
| For PEAK LOAD the calculated MILLION Btu per hour for assumed boiler is: | 5.022 |  | 400 HP | 875000 | 805000
| Note: Wood fueled systems operate more efficently when load is close to system capacity. |  |  | 450 HP | 900000 | 830000
| Calculated the average load as a percentage of system capacity is: | 47.29% |  | 500 HP | 940000 | 865000
| Ideally the average load should be at least 67% system capacity. Low loads can present problems. |  |  | 550 HP | 975000 | 900000
|  |  |  | 600 HP | 1010000 | 935000
| NOTE: The table to the right provides some ROUGH estimates of wood/bark fueled boiler |  |  | 650 HP | 1050000 | 970000
| system costs for various boiler sizes. This is a ROUGH estimation of what might be expected as |  |  | 700 HP | 1090000 | 1005000
| an installed wood/bark fuel boiler system, to include the low pressure steam boiler, the fuel |  |  | 750 HP | 1135000 | 1050000
| stoker and combustion device, flue gas cleaning system, steam piping with water side auxiliaries, |  |  | 800 HP | 1170000 | 1080000
| assembly, installation, start-up and operator training. As a general rule of thumb, |  |  | 850 HP | 1200000 | 1110000
| for each 50 horsepower of the boiler system, approximately a 2,000 cubic foot area |  |  | 900 HP | 1230000 | 1140000
| is required for wood fuel receiving, metering and storage for a 3 day fuel supply. |  |  | 950 HP | 1265000 | 1170000
| THESE COST DATA ARE SUITABLE FOR ROUGH PRELIMINARY ESTIMATES ONLY!!!!!! |  |  | 1000 HP | 1300000 | 1200000
For preliminary payback estimates associated with the wood or bark fueled boiler system,
in considering a wood fueled system in lieu of "identical" system replacement of the existing system (e.g. same fuel type and efficiency)
OR in considering a wood fueled system in lieu of system replacement with a different system (e.g. different fuel type and efficiency)
the difference in the costs of the two systems (i.e. the excess investment cost associated with the wood system) is the incremental investment.
NOTE: If the system that is being considered as the alternate to the wood system is a significantly upgraded or otherwise different system.....
ensure that the analysis reflects those appropriate values under the "current" operational assumptions.
Simply, where the wood or bark fueled system is being considered as an alternate to another system which would be installed anyway,
the annual operational cost (savings) associated with the wood or bark fuel would be considered against the DIFFERENCE in the
total investment associated with the two systems. (i.e. the incremental investment in the wood system)
HOWEVER......
If the existing system is in good condition, has considerable remaining life, and does not now require major (costly) repairs to extend the system life...
Then essentially the incremental investment in the wood system would be the full cost of the wood system, less any salvage value,
plus any savings associated with avoided repairs immediately needed on the existing system.
Some important points need to be considered regarding use of "PAYBACK" estimates, even for very preliminary analyses:
In considering the incremental investment difference, the economic lives of the two alternatives should be similar.
There are some technical problems associated with payback analysis including that it does not consider the time value of money.
None-the-less, payback analysis is widely used in preliminary analyses for many good reasons, but it should not be a sole decision criteria.
PRELIMINARY PAYBACK ESTIMATES FOR THE WOOD OR BARK BOILER SYSTEM
Assuming the incremental investment for the wood boiler system is known:
e> | What is the estimated incremental investment for the wood or bark boiler system? | 200000
| Estimated "payback" period (in years) to recover incremental investment is: | 2.364
Assuming the incremental investment for the wood boiler system is not known:
e> | What is the maximum "payback" period (in years) required to recover incremental investment? | 7
| Estimated maximum incremental investment for the wood or bark boiler system is: | 592220.4167
Some notes regarding interpretation of the preliminary payback analysis:
If according to the decision criteria being used, the payback period required to recover the incremental investment is excessively long,
OR,
if according to the maximum payback period you would be willing to accept, the maximum incremental investment is unrealistically low,
THEN
the operational cost savings associated with a wood or bark fueled boiler does not likely justify the investment at this time,
BUT,
if circumstances change, such as the existing system fails and must be replaced, or costs of operation increase significantly,
THEN,
perhaps the analysis of a wood or bark fuel system should be reconsidered at that time (or otherwise prior to major facility renovations).
HOWEVER,
If according to the decision criteria being used, the payback period required to recover the incremental investment is short enough,
OR,
if according to the maximum payback period you would be willing to accept, a realistic value for incremental investment is acceptable,
THEN
the operational cost savings associated with a wood or bark fueled boiler COULD justify the required incremental investment at this time,
AND IF SO, further analysis is justified.
PRELIMINARY ECONOMIC ANALYSIS OF A WOOD OR BARK FUELED BOILER SYSTEM - FOLLOW-ON PRELIMINARY ASSESSMENT
Within the follow-on preliminary assessment - on rows where the code "e>" is shown in column A, an entry is to be made in one or more columns.
Entry numbers in the rows are included - BUT these are ONLY for illustrative purposes, they should NOT be considered as suitable estimates for your analysis.
The ONLY exception is where data is shown that was calculated in your INITIAL ASSESSMENT above, and is clearly labeled as such.
These data should also be checked and different assumptions used in entries if appropriate to the analysis.
Within the following section of the spreadsheet, entries may in some circumstances be made only in a single column, HOWEVER,
in some other areas, entries may be required in 20 columns in a single row to reflect assumptions pertaining to a 20 year analysis.
This section of the spreadsheet is MUCH more complicated than the INITIAL ASSESSMENT section and requires considerable assumptions specific to the analysis.
This FOLLOW-ON PRELIMINARY ASSESSMENT section will estimate a NET PRESENT VALUE of the incremental investment for a 20 year analysis period.
It is assumed that persons continuing with this section of the spreadsheet will usually have some considerable familiarity with such analyses.
This section of the spreadsheet is MUCH more complicated than the INITIAL ASSESSMENT section and requires considerable assumptions specific to the analysis.
Prior to continuing, it is recommended the user scan down the spreadsheet to get an appreciation for the type of information required for the FOLLOW-ON.
IT IS ASSUMED THAT MANY USERS WHO HAVE COMPLETED INITIAL ASSESSMENT SECTION MAY DESIRE SOME ASSISTANCE TO CONTINUE IN A FOLLOW-ON ANALYSIS.
ASSUMPTIONS REGARDING BOILER OPERATIONAL COST DATA
BOILER RELATED PAYROLL DATA - EXISTING OR ALTERNATE SYSTEM
e>> | Average # of employees working with boiler related duties 1st shift |  |  | 0.25
e>> | Average # of employees working with boiler related duties 2nd shift |  |  | 0
e>> | Average # of employees working with boiler related duties 3rd shift |  |  | 0
e>> | Average # of employees working with boiler related duties 4th shift |  |  | 0
| AVERAGE # OF BOILER RELATED EMPLOYEES, ALL SHIFTS COMBINED |  |  | 0.25
| Assumed # days boiler is used per year (for analysis) is? |  |  | 365
e>> | Average # of days (not including overtime) an employee works (boiler related) per year |  |  | 245
e>> | Average base hourly wage of boiler related employees |  |  | 10.25
e>> | Fringe benefits for employees as a % of base hourly wage |  |  | 25%
e>> | Overtime premium for employees as a % of base hourly wage |  |  | 50%
e>> | Fringe benefits for overtime hours a % of the overtime hourly wage |  |  | 20%
e>> | Normal # of boiler related paid hours per shift (not including overtime) |  |  | 3
e>> | Average # of overtime hours per boiler related employee per month boiler is operated |  |  | 4
| AVERAGE # OF OVERTIME HOURS PER BOILER RELATED EMPLOYEE PER YEAR |  |  | 48
e>> | Other boiler related payroll expenses in total dollars per year |  |  | 0
SUMMARY OF ESTIMATED ANNUAL BOILER RELATED LABOR COSTS FIRST FULL YEAR - EXISTING OR ALTERNATE SYSTEM
| ANNUAL PAYROLL BREAKDOWN | DOLLARS | PERCENT
| BASE WAGES | 1883.4375 | 73.12%
| FRINGE BENEFITS | 470.8594 | 18.28%
| OVERTIME WAGES | 184.5 | 7.163%
| OVERTIME FRINGE | 36.9 | 1.433%
| OTHER PAYROLL | 0 | 0%
| TOTAL PAYROLL | 2575.6969 | 100%
| BOILER RELATED LABOR $/DAY OF BOILER OPERATION | 7.0567
BOILER RELATED PAYROLL DATA - WOOD OR BARK FUELED SYSTEM
e>> | Average # of employees working with boiler related duties 1st shift |  |  | 0.75
e>> | Average # of employees working with boiler related duties 2nd shift |  |  | 0
e>> | Average # of employees working with boiler related duties 3rd shift |  |  | 0
e>> | Average # of employees working with boiler related duties 4th shift |  |  | 0
| AVERAGE # OF BOILER RELATED EMPLOYEES, ALL SHIFTS COMBINED |  |  | 0.75
| Assumed # days boiler is used per year (for analysis) is? |  |  | 365
e>> | Average # of days (not including overtime) an employee works (boiler related) per year |  |  | 245
e>> | Average base hourly wage of boiler related employees |  |  | 10.25
e>> | Fringe benefits for employees as a % of base hourly wage |  |  | 25%
e>> | Overtime premium for employees as a % of base hourly wage |  |  | 50%
e>> | Fringe benefits for overtime hours a % of the overtime hourly wage |  |  | 20%
e>> | Normal # of boiler related paid hours per shift (not including overtime) |  |  | 6
e>> | Average # of overtime hours per boiler related employee per month boiler is operated |  |  | 16
| AVERAGE # OF OVERTIME HOURS PER BOILER RELATED EMPLOYEE PER YEAR |  |  | 192
e>> | Other boiler related payroll expenses in total dollars per year |  |  | 0
SUMMARY OF ESTIMATED ANNUAL BOILER RELATED LABOR COSTS FIRST FULL YEAR - WOOD OR BARK FUELED SYSTEM
| ANNUAL PAYROLL BREAKDOWN | DOLLARS | PERCENT
| BASE WAGES | 11300.625 | 67.34%
| FRINGE BENEFITS | 2825.1562 | 16.83%
| OVERTIME WAGES | 2214 | 13.19%
| OVERTIME FRINGE | 442.8 | 2.638%
| OTHER PAYROLL | 0 | 0%
| TOTAL PAYROLL | 16782.5812 | 100%
| BOILER RELATED LABOR $/DAY OF BOILER OPERATION | 45.9797
ESTIMATED INCREASED ANNUAL BOILER RELATED LABOR COSTS FIRST FULL YEAR - FOR THE WOOD OR BARK FUELED SYSTEM
INCREASE IN ANNUAL PAYROLL REQUIRED FOR WOOD FUELED SYSTEM
| ANNUAL PAYROLL DIFFERENCE BREAKDOWN | DOLLARS
| INCREASE IN BASE WAGES | 9417.1875
| INCREASE IN FRINGE BENEFITS | 2354.2969
| INCREASE IN OVERTIME WAGES | 2029.5
| INCREASE IN OVERTIME FRINGE | 405.9
| INCREASE IN OTHER PAYROLL | 0
| INCREASE IN TOTAL PAYROLL FOR YEAR WITH WOOD FUELED SYSTEM | 14206.8844
| INCREASE IN TOTAL PAYROLL WITH WOOD FUELED SYSTEM PER MILLION BTU NET | 0.64872
| INCREASE IN BOILER RELATED LABOR $/DAY OF BOILER OPERATION | 38.923
OTHER COSTS OF BOILER OPERATION (EXCEPT FUEL AND FIXED COSTS)
INCREASE (DIFFERENCE) IN OPERATIONAL COSTS PER YEAR ASSOCIATED WITH THE WOOD FUEL SYSTEM
| ITEM | $/YEAR
e>> | Increased Electricity | 1000
e>> | Increased Rolling Stock Maintenance/Repair | 200
e>> | Increased Boiler Maintenance/Repair | 1000
e>> | Increased Other Maintenance/Repair | 1000
e>> | Increased Ash/Waste Disposal Costs | 1000
e>> | Increased Chemicals | 500
e>> | Increased Operating Supplies | 750
e>> | Increased Fuel for Rolling Stock | 600 |  | e>>
e>> | Net increase in other operational cost per year | 0 | Specify >
| INCREASE IN TOTAL OTHER VARIABLE COST YEAR WITH WOOD FUELED SYSTEM | 6050
| INCREASE IN TOTAL OTHER VAR. COST WITH WOOD SYSTEM PER MILLION BTU NET | 0.27626
| INCREASE IN BOILER RELATED OTHER VARIABLE COST $/DAY OF BOILER OPERATION | 16.5753
INCREASE (DIFFERENCE) ASSOCIATED WITH WOOD FUELED SYSTEM IN OPERATING FIXED COSTS FOR FIRST FULL YEAR (does not include interest & depreciation)
| ITEM | $/YEAR
e>> | Increased Insurance | 200
e>> | Increased Property Taxes | 0
e>> | Increased Security | 0
e>> | Increased Administrative/Accounting/Legal | 200
e>> | Increased Salary & Benefits (office & management) | 0 |  | e>>
e>> | All other increases in fixed costs in $/year | 0 | Specify >
| INCREASE IN TOTAL FIXED COSTS $/YEAR ASSOCIATED WITH WOOD FUELED SYSTEM | 400 | <<^(NOTE: Should not include interest & depreciation)
SUMMARY OF FUEL REQUIREMENTS AND COST CALCULATIONS FROM PRIOR ESTIMATES
| Total MILLION Btu (net) required per Day is: | 60
| Assumed # days boiler is used per year (for analysis) is: | 365
| Calculated MILLION Btu (net) that are required per YEAR is: | 21900
FOR THE CURRENT SYSTEM (OR ALTERNATIVE TO WOOD-BARK FUELED SYSTEM)
| Cost per net MILLION Btu of current (or alternate) fuel is: | 8.5
| Calculated Average Fuel Cost per Year - current (or alternative) system | 186150
FOR THE WOOD/BARK FUELED SYSTEM
| Calculated cost per net MILLION Btu of wood or bark boiler system is: | 3.4722
| Fraction of annual Btu needs to be supplied by the wood system is: | 95% | this would be 100% if no backup system is used
| Calculated fuel cost per YEAR for the wood or bark boiler system is: | 72239.5833
| Fraction of annual Btu needs to be supplied by a backup system % is: | 5%
| Cost per net MILLION Btu of fuel for the backup boiler system? | 8.5
| Calculated fuel cost per YEAR for the backup boiler system is: | 9307.5
| Calculated average TOTAL fuel cost per YEAR for the wood system is: | 81547.0833 | note: this includes both wood/bark fuel and backup boiler fuel
SUMMARY OF INPUTS INTO ANALYSIS FOR PERIOD # 2 (FIRST FULL YEAR)
NOTE: The items in column E under the label "ENTRY" are reflecting a relative address of items which are in column C under the label "CALCULATED".
If you change nothing, these "calculated" values will become the "entry" values for the first full year (period or year #2) of the following financial analysis.
HOWEVER - If adjustments to first full year values (year #2) are desired they can be made directly within the "ENTRY" area of column E.
This structure of an attached link that may be easily broken and re-attached is designed to facilitate easy heuristic ("what if?") analyses.
In this fashion, any or all of the key assumption variables calculated for use in the analysis may be directly modified to a desired value.
The side-by-side comparison of calculated vs entry values serves to quickly flag that such heuristic experimentation is being conducted.
e>> (IMPORTANT - see note above)
|  | CALCULATED |  | ENTRY
e>> | MILLION Btu (net) that are required per YEAR is: | 21900 |  | 21900
e>> | Cost per net MILLION Btu of current (or alternate) fuel is: | 8.5 |  | 8.5
e>> | Cost per net MILLION Btu of wood or bark boiler system is: | 3.4722 |  | 3.4722
e>> | Cost per net MILLION Btu of fuel for the backup boiler system? | 8.5 |  | 8.5
e>> | Fraction of annual Btu needs to be supplied by the wood system is: | 95% |  | 95%
e>> | Increase in Total Payroll With the Wood Fueled System Per MILLION Btu Net | 0.64872 |  | 0.64872
e>> | Increase in Total Other Variable Costs With the Wood Fueled System Per MILLION Btu Net | 0.27626 |  | 0.27626
e>> | Increase in Total Fixed Costs With the Wood Fueled System in Total $/Year | 400 |  | 400
PERIOD INPUTS INTO ECONOMIC MODEL
NOTE: The data under "ENTRY" in column E above will automatically be reflected as the values for the first full year (Year #2) in the entries below.
An entry is required in all other cells of each row in each column, for items in Year #1 & Year 3-20 with entry as a % of the item value entered for year # 2.
The percentage change entry format convention is used as it is generally easier for most people.
These data will be transformed to values in the "Key Production Data" section below.
|  | YEAR #1 | YEAR #2 | YEAR #3 | YEAR #4 | YEAR #5 | YEAR #6 | YEAR #7 | YEAR #8 | YEAR #9 | YEAR #10 | YEAR #11 | YEAR #12 | YEAR #13 | YEAR #14 | YEAR #15 | YEAR #16 | YEAR #17 | YEAR #18 | YEAR #19 | YEAR #20
e>> | MILLION Btu (net) that are required per YEAR is: | 75% | 21900 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
e>> | Cost per net MILLION Btu of current (or alternate) fuel is: | 100% | 8.5 | 104% | 108.2% | 112.5% | 117% | 121.7% | 126.5% | 131.6% | 136.9% | 142.3% | 148% | 153.9% | 160.1% | 166.5% | 173.2% | 180.1% | 187.3% | 194.8% | 202.6%
e>> | Cost per net MILLION Btu of wood or bark boiler system is: | 100% | 3.4722 | 104% | 108.2% | 112.5% | 117% | 121.7% | 126.5% | 131.6% | 136.9% | 142.3% | 148% | 153.9% | 160.1% | 166.5% | 173.2% | 180.1% | 187.3% | 194.8% | 202.6%
e>> | Cost per net MILLION Btu of fuel for the backup boiler system? | 100% | 8.5 | 104% | 108.2% | 112.5% | 117% | 121.7% | 126.5% | 131.6% | 136.9% | 142.3% | 148% | 153.9% | 160.1% | 166.5% | 173.2% | 180.1% | 187.3% | 194.8% | 202.6%
e>> | Fraction of annual Btu needs to be supplied by the wood system is: | 80% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95%
e>> | Increase in Total Payroll With the Wood Fueled System Per MILLION Btu Net | 100% | 0.64872 | 104% | 108.2% | 112.5% | 117% | 121.7% | 126.5% | 131.6% | 136.9% | 142.3% | 148% | 153.9% | 160.1% | 166.5% | 173.2% | 180.1% | 187.3% | 194.8% | 202.6%
e>> | Increase in Total Other Variable Costs With the Wood Fueled System Per MILLION Btu Net | 100% | 0.27626 | 103% | 106.1% | 109.3% | 112.6% | 115.9% | 119.4% | 123% | 126.7% | 130.5% | 134.4% | 138.4% | 142.6% | 146.9% | 151.3% | 155.8% | 160.5% | 165.3% | 170.2%
e>> | Increase in Total Fixed Costs With the Wood Fueled System in Total $/Year | 100% | 400 | 103% | 106.1% | 109.3% | 112.6% | 115.9% | 119.4% | 123% | 126.7% | 130.5% | 134.4% | 138.4% | 142.6% | 146.9% | 151.3% | 155.8% | 160.5% | 165.3% | 170.2%
KEY PRODUCTION DATA FOR ENTRY INTO MODEL
|  | YEAR #1 | YEAR #2 | YEAR #3 | YEAR #4 | YEAR #5 | YEAR #6 | YEAR #7 | YEAR #8 | YEAR #9 | YEAR #10 | YEAR #11 | YEAR #12 | YEAR #13 | YEAR #14 | YEAR #15 | YEAR #16 | YEAR #17 | YEAR #18 | YEAR #19 | YEAR #20
| MILLION Btu (net) that are required per YEAR is: | 16425 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900
| Cost per net MILLION Btu of current (or alternate) fuel is: | 8.5 | 8.5 | 8.84 | 9.1936 | 9.5613 | 9.9438 | 10.3415 | 10.7552 | 11.1854 | 11.6328 | 12.0982 | 12.5821 | 13.0854 | 13.6088 | 14.1531 | 14.7192 | 15.308 | 15.9203 | 16.5572 | 17.2194
| Cost per net MILLION Btu of wood or bark boiler system is: | 3.4722 | 3.4722 | 3.6111 | 3.7556 | 3.9058 | 4.062 | 4.2245 | 4.3935 | 4.5692 | 4.752 | 4.9421 | 5.1397 | 5.3453 | 5.5591 | 5.7815 | 6.0128 | 6.2533 | 6.5034 | 6.7635 | 7.0341
| Cost per net MILLION Btu of fuel for the backup boiler system? | 8.5 | 8.5 | 8.84 | 9.1936 | 9.5613 | 9.9438 | 10.3415 | 10.7552 | 11.1854 | 11.6328 | 12.0982 | 12.5821 | 13.0854 | 13.6088 | 14.1531 | 14.7192 | 15.308 | 15.9203 | 16.5572 | 17.2194
| Fraction of annual Btu needs to be supplied by the wood system is: | 80% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95%
| Increase in Total Payroll With the Wood Fueled System Per MILLION Btu Net | 10655.1633 | 14206.8844 | 14775.1598 | 15366.1661 | 15980.8128 | 16620.0453 | 17284.8471 | 17976.241 | 18695.2906 | 19443.1023 | 20220.8263 | 21029.6594 | 21870.8458 | 22745.6796 | 23655.5068 | 24601.7271 | 25585.7961 | 26609.228 | 27673.5971 | 28780.541
| Increase in Total Other Variable Costs With the Wood Fueled System Per MILLION Btu Net | 4537.5 | 6050 | 6231.5 | 6418.445 | 6610.9983 | 6809.3283 | 7013.6081 | 7224.0164 | 7440.7369 | 7663.959 | 7893.8778 | 8130.6941 | 8374.6149 | 8625.8534 | 8884.629 | 9151.1678 | 9425.7029 | 9708.474 | 9999.7282 | 10299.72
| Increase in Total Fixed Costs With the Wood Fueled System in Total $/Year | 400 | 400 | 412 | 424.36 | 437.0908 | 450.2035 | 463.7096 | 477.6209 | 491.9495 | 506.708 | 521.9093 | 537.5666 | 553.6935 | 570.3044 | 587.4135 | 605.0359 | 623.187 | 641.8826 | 661.1391 | 680.9732
CAPITAL INVESTMENTS AND SIMPLIFIED ESTIMATION OF DEPRECIATION
REMINDER - Where an analysis is conducted as an incremental analysis, the incremental investment associated with the wood or bark fueled system should be used.
NOTE: The model estimates depreciation for investments in the different property classes using the MACRS GDS system with 200% DB and half-year convention.
To do this, the total INITIAL investment in the different property classes is simply entered below in column C as appropriate.
IF ANY OTHER DEPRECIATION METHOD IS DESIRED - the appropriate values for non-depreciable property and working capital should still be entered, AND
any other appropriate depreciation values may be directly entered in either of the two rows below labeled "OTHER DEPRECIATION IN YEAR".
| DEPRECIATION INFORMATION | YEAR #1: e>>
| Total in MACRS year category GDS System 200% | YEAR #1: YEAR #1; YEAR #2: as % of Total initial investment
e>> | 3 Year Recovery GDS (MACRS) Property | YEAR #1: 0; YEAR #2: 0%
e>> | 5 Year Recovery GDS (MACRS) Property | YEAR #1: 10000; YEAR #2: 4.739%
e>> | 7 Year Recovery GDS (MACRS) Property | YEAR #1: 200000; YEAR #2: 94.79%
e>> | 10 Year Recovery GDS (MACRS) Property | YEAR #1: 0; YEAR #2: 0%
e>> | 15 Year Recovery GDS (MACRS) Property | YEAR #1: 0; YEAR #2: 0%
e>> | 20 Year Recovery GDS (MACRS) Property | YEAR #1: 0; YEAR #2: 0%
e>> | Non-Depreciable (e.g. land) | YEAR #1: 1000; YEAR #2: 0.4739%
| TOTAL INITIAL INVESTMENT (except working capital) >>> | YEAR #1: 211000; YEAR #2: 100%
e>> | Initial Working Capital | YEAR #1: 4000
ASSUMED DEPRECIATION TAKEN IN PERIOD (first yr in service = year #1, second year in service = year #2, etc.)
| PROPERTY TYPE | YEAR #1 | YEAR #2 | YEAR #3 | YEAR #4 | YEAR #5 | YEAR #6 | YEAR #7 | YEAR #8 | YEAR #9 | YEAR #10 | YEAR #11 | YEAR #12 | YEAR #13 | YEAR #14 | YEAR #15 | YEAR #16 | YEAR #17 | YEAR #18 | YEAR #19 | YEAR #20
| 3 Year Recovery GDS (MACRS) Property | YEAR #1: 33.33%; YEAR #2: 44.45%; YEAR #3: 14.81%; YEAR #4: 7.41%
| 5 Year Recovery GDS (MACRS) Property | YEAR #1: 20%; YEAR #2: 32%; YEAR #3: 19.2%; YEAR #4: 11.52%; YEAR #5: 11.52%; YEAR #6: 5.76%
| 7 Year Recovery GDS (MACRS) Property | YEAR #1: 14.29%; YEAR #2: 24.49%; YEAR #3: 17.49%; YEAR #4: 12.49%; YEAR #5: 8.93%; YEAR #6: 8.92%; YEAR #7: 8.93%; YEAR #8: 4.46%
| 10 Year Recovery GDS (MACRS) Property | YEAR #1: 10%; YEAR #2: 18%; YEAR #3: 14.4%; YEAR #4: 11.52%; YEAR #5: 9.22%; YEAR #6: 7.37%; YEAR #7: 6.55%; YEAR #8: 6.55%; YEAR #9: 6.56%; YEAR #10: 6.55%; YEAR #11: 3.28%
| 15 Year Recovery GDS (MACRS) Property | 5% | 9.5% | 8.55% | 7.7% | 6.93% | 6.23% | 5.9% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 5.91% | 2.95%
| 20 Year Recovery GDS (MACRS) Property | 3.75% | 7.219% | 6.677% | 6.177% | 5.713% | 5.285% | 4.888% | 4.522% | 4.462% | 4.461% | 4.462% | 4.461% | 4.462% | 4.461% | 4.462% | 4.461% | 4.462% | 4.461% | 4.462% | 4.461%
TOTAL VALUE OF DEPRECIATION ENTERED INTO MODEL FOR YEAR
| YEAR ACQUIRED | YEAR #1 | YEAR #2 | YEAR #3 | YEAR #4 | YEAR #5 | YEAR #6 | YEAR #7 | YEAR #8 | YEAR #9 | YEAR #10 | YEAR #11 | YEAR #12 | YEAR #13 | YEAR #14 | YEAR #15 | YEAR #16 | YEAR #17 | YEAR #18 | YEAR #19 | YEAR #20
| INITIAL INVESTMENT GDS (MACRS) PROPERTY ACQUIRED YEAR #1 (automatic from above) | 30580 | 52180 | 36900 | 26132 | 19012 | 18416 | 17860 | 8920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e>> | OTHER DEPRECIATION IN YEAR (optional entry)
e>> | OTHER DEPRECIATION IN YEAR (optional entry)
| TOTAL DEPRECIATION IN YEAR | 30580 | 52180 | 36900 | 26132 | 19012 | 18416 | 17860 | 8920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(NOTE: Under optional entry rows above, depreciation for other than Yr#1 must be manually entered, OR enter that year first as if it was a value for year #1, then copy and paste annual dollar values as appropriate.)
CAPITAL INVESTMENT SUMMARY
(NOTE: All standard Year #1 investments, including year #1 working capital, are entered automatically. Total investments in all other years (if any) must be manually entered.)
|  | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR # | YEAR #
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
e>> | TOTAL INVESTMENT YEAR (automatic calculation for standard year #1 investment) | 215000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL INVESTMENTS ALL YEARS | 1: 215000
| NPV TOTAL INVESTMENT IN YEAR | 215000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NPV TOTAL INVESTMENTS ALL YEARS | 1: 215000
| TOTAL DEPRECIATION ALL YEARS | 1: 210000
| INITIAL WORKING CAPITAL | 1: 4000
| NON-DEPRECIABLE ASSETS | 1: 1000
e>> | Est. Salvage Value of Non-Deprec. Assets | 1: 2000; 2: << at end of year #20
| RESIDUAL "BOOK" OF DEP. ASSETS | 1: 0
e>> | Est. Salvage Value of Depreciable Assets | 1: 20000; 2: << at end of year #20
| ASSETS SUBJ.TO CAPITAL GAINS TAX | 1: 21000; 2: << at end of year #20
e>> | Corporate tax rate as a % of income | 1: 42%
e>> | Capital Gains Tax Rate | 1: 20%
LOAN INFORMATION (AMOUNT, INTEREST, MINIMUM P&I, ETC.)
e>> | Original Loan | 1: 200000
e>> | Nominal interest rate per year | 1: 7.5%
e>> | # Compounding periods/yr | 1: 12
| EFFECTIVE ANNUAL INTEREST RATE | 1: 7.763%
e>> | Period of Loan (years) | 1: 10
| REQ. MINIMUM P&I PAYMENT/YR (est.) | 1: 29488.4058
FINANCIAL SUMMARY ANALYSIS
|  | YEAR #1 | YEAR #2 | YEAR #3 | YEAR #4 | YEAR #5 | YEAR #6 | YEAR #7 | YEAR #8 | YEAR #9 | YEAR #10 | YEAR #11 | YEAR #12 | YEAR #13 | YEAR #14 | YEAR #15 | YEAR #16 | YEAR #17 | YEAR #18 | YEAR #19 | YEAR #20
| MILLION Btu (net) THAT ARE REQUIRED PER YEAR IS: | 16425 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900 | 21900
| FUEL COST FOR THE YEAR IF CURRENT OR ALTERNATE FUEL WAS USED | 139612.5 | 186150 | 193596 | 201339.84 | 209393.4336 | 217769.1709 | 226479.9378 | 235539.1353 | 244960.7007 | 254759.1287 | 264949.4939 | 275547.4736 | 286569.3726 | 298032.1475 | 309953.4334 | 322351.5707 | 335245.6336 | 348655.4589 | 362601.6772 | 377105.7443
| TOTAL FUEL COST WITH THE WOOD FIRED SYSTEM (AND BACKUP) | 73547.5 | 81547.0833 | 84808.9667 | 88201.3253 | 91729.3783 | 95398.5535 | 99214.4956 | 103183.0754 | 107310.3985 | 111602.8144 | 116066.927 | 120709.6041 | 125537.9882 | 130559.5077 | 135781.8881 | 141213.1636 | 146861.6901 | 152736.1577 | 158845.604 | 165199.4282
| ANNUAL INCREASE IN VARIABLE LABOR COST WITH WOOD SYSTEM | 10655.1633 | 14206.8844 | 14775.1598 | 15366.1661 | 15980.8128 | 16620.0453 | 17284.8471 | 17976.241 | 18695.2906 | 19443.1023 | 20220.8263 | 21029.6594 | 21870.8458 | 22745.6796 | 23655.5068 | 24601.7271 | 25585.7961 | 26609.228 | 27673.5971 | 28780.541
| ANNUAL INCREASE IN OTHER VARIABLE COST WITH WOOD SYSTEM | 4537.5 | 6050 | 6231.5 | 6418.445 | 6610.9983 | 6809.3283 | 7013.6081 | 7224.0164 | 7440.7369 | 7663.959 | 7893.8778 | 8130.6941 | 8374.6149 | 8625.8534 | 8884.629 | 9151.1678 | 9425.7029 | 9708.474 | 9999.7282 | 10299.72
| OPERATIONAL COST SAVINGS ASSOCIATED WITH THE WOOD SYSTEM ($/YEAR) | 50872.3367 | 84346.0323 | 87780.3736 | 91353.9035 | 95072.2441 | 98941.2439 | 102966.9869 | 107155.8025 | 111514.2747 | 116049.2531 | 120767.8628 | 125677.5161 | 130785.9237 | 136101.1068 | 141631.4096 | 147385.5122 | 153372.4444 | 159601.5992 | 166082.7479 | 172826.0551
| OPERATIONAL COST SAVINGS FOR THE WOOD SYSTEM (%/ ALTERNATE FUEL FOR YEAR) | 36.44% | 45.31% | 45.34% | 45.37% | 45.4% | 45.43% | 45.46% | 45.49% | 45.52% | 45.55% | 45.58% | 45.61% | 45.64% | 45.67% | 45.69% | 45.72% | 45.75% | 45.78% | 45.8% | 45.83%
e>> | other associated net revenue (or operational cost savings) subject to normal tax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL FUEL COST SAVINGS WITH THE WOOD FIRED SYSTEM (AND OTHER REVENUE) | 66065 | 104602.9167 | 108787.0333 | 113138.5147 | 117664.0553 | 122370.6175 | 127265.4422 | 132356.0598 | 137650.3022 | 143156.3143 | 148882.5669 | 154837.8696 | 161031.3844 | 167472.6397 | 174171.5453 | 181138.4071 | 188383.9434 | 195919.3012 | 203756.0732 | 211906.3161
| TOTAL INCREASE IN NON-FUEL VARIABLE COST/YEAR WITH WOOD SYSTEM | 15192.6633 | 20256.8844 | 21006.6597 | 21784.6111 | 22591.8111 | 23429.3736 | 24298.4553 | 25200.2574 | 26136.0275 | 27107.0613 | 28114.7041 | 29160.3535 | 30245.4607 | 31371.533 | 32540.1358 | 33752.8949 | 35011.499 | 36317.702 | 37673.3253 | 39080.261
| TOTAL INCREASE IN FIXED COST/YEAR WITH WOOD SYSTEM | 400 | 400 | 412 | 424.36 | 437.0908 | 450.2035 | 463.7096 | 477.6209 | 491.9495 | 506.708 | 521.9093 | 537.5666 | 553.6935 | 570.3044 | 587.4135 | 605.0359 | 623.187 | 641.8826 | 661.1391 | 680.9732
| INTEREST ON LOAN | 15526.5198 | 14442.6223 | 13274.579 | 12015.8575 | 10659.4181 | 9197.6749 | 7622.4527 | 5924.9419 | 4095.649 | 2124.3433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| INCREASE IN NET PROFIT BEFORE DEPREC. & TAX (SAVINGS WITH WOOD SYSTEM) | 34945.8169 | 69503.41 | 74093.7946 | 78913.6861 | 83975.7352 | 89293.3655 | 94880.8246 | 100753.2396 | 106926.6762 | 113418.2018 | 120245.9535 | 125139.9495 | 130232.2301 | 135530.8024 | 141043.9961 | 146780.4764 | 152749.2574 | 158959.7166 | 165421.6089 | 172145.0819
| TOTAL DEPRECIATION INCREASE ASSOCIATED WITH WOOD SYSTEM | 30580 | 52180 | 36900 | 26132 | 19012 | 18416 | 17860 | 8920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHANGE IN TAXABLE INCOME ASSOCATED WITH WOOD SYSTEM | 4365.8169 | 17323.41 | 37193.7946 | 52781.6861 | 64963.7352 | 70877.3655 | 77020.8246 | 91833.2396 | 106926.6762 | 113418.2018 | 120245.9535 | 125139.9495 | 130232.2301 | 135530.8024 | 141043.9961 | 146780.4764 | 152749.2574 | 158959.7166 | 165421.6089 | 172145.0819
| TAX | 1833.6431 | 7275.8322 | 15621.3937 | 22168.3081 | 27284.7688 | 29768.4935 | 32348.7463 | 38569.9606 | 44909.204 | 47635.6447 | 50503.3005 | 52558.7788 | 54697.5367 | 56922.937 | 59238.4784 | 61647.8001 | 64154.6881 | 66763.081 | 69477.0757 | 72300.9344
| CHANGE IN (operational) AFTER TAX PROFIT (LOSS) DUE TO WOOD SYSTEM | 2532.1738 | 10047.5778 | 21572.4009 | 30613.3779 | 37678.9664 | 41108.872 | 44672.0782 | 53263.279 | 62017.4722 | 65782.557 | 69742.653 | 72581.1707 | 75534.6935 | 78607.8654 | 81805.5177 | 85132.6763 | 88594.5693 | 92196.6357 | 95944.5331 | 99844.1475
| CHANGE IN (operational) AFTER TAX NET CASH FLOW WITH WOOD SYSTEM | 33112.1738 | 62227.5778 | 58472.4009 | 56745.3779 | 56690.9664 | 59524.872 | 62532.0782 | 62183.279 | 62017.4722 | 65782.557 | 69742.653 | 72581.1707 | 75534.6935 | 78607.8654 | 81805.5177 | 85132.6763 | 88594.5693 | 92196.6357 | 95944.5331 | 99844.1475
e>> | other net revenue or equivalent positive cash flows NOT subject to capital gains tax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e>> | other net revenue subject to capital gains tax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21000
| CAPITAL GAINS TAX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4200
| CHANGE IN AFTER TAX NET CASH FLOW WITH WOOD SYSTEM | 33112.1738 | 62227.5778 | 58472.4009 | 56745.3779 | 56690.9664 | 59524.872 | 62532.0782 | 62183.279 | 62017.4722 | 65782.557 | 69742.653 | 72581.1707 | 75534.6935 | 78607.8654 | 81805.5177 | 85132.6763 | 88594.5693 | 92196.6357 | 95944.5331 | 116644.1475
| MINIMUM LOAN PRINCIPAL REPAYMENT | 13961.8861 | 15045.7836 | 16213.8269 | 17472.5484 | 18828.9877 | 20290.731 | 21865.9531 | 23563.4639 | 25392.7568 | 27364.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
e>> | Additional loan principal repayment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CHANGE IN NET ADDITION TO RETAINED EARNINGS WITH WOOD SYSTEM | 19150.2878 | 47181.7942 | 42258.574 | 39272.8295 | 37861.9787 | 39234.141 | 40666.1251 | 38619.8151 | 36624.7153 | 38418.4945 | 69742.653 | 72581.1707 | 75534.6935 | 78607.8654 | 81805.5177 | 85132.6763 | 88594.5693 | 92196.6357 | 95944.5331 | 116644.1475
SUMMARY OF LOAN INFORMATION
|  | YEAR #1 | YEAR #2 | YEAR #3 | YEAR #4 | YEAR #5 | YEAR #6 | YEAR #7 | YEAR #8 | YEAR #9 | YEAR #10 | YEAR #11 | YEAR #12 | YEAR #13 | YEAR #14 | YEAR #15 | YEAR #16 | YEAR #17 | YEAR #18 | YEAR #19 | YEAR #20
| BEGINNING PRINCIPAL DUE | 200000 | 186038.1139 | 170992.3303 | 154778.5035 | 137305.9551 | 118476.9674 | 98186.2364 | 76320.2833 | 52756.8194 | 27364.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MINIMUM PRINCIPAL REPAYMENT | 13961.8861 | 15045.7836 | 16213.8269 | 17472.5484 | 18828.9877 | 20290.731 | 21865.9531 | 23563.4639 | 25392.7568 | 27364.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ADDITIONAL PRINCIPAL REPAYMENT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ENDING PRINCIPAL DUE | 186038.1139 | 170992.3303 | 154778.5035 | 137305.9551 | 118476.9674 | 98186.2364 | 76320.2833 | 52756.8194 | 27364.0626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| INTEREST PAYMENTS | 15526.5198 | 14442.6223 | 13274.579 | 12015.8575 | 10659.4181 | 9197.6749 | 7622.4527 | 5924.9419 | 4095.649 | 2124.3433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CALCULATION OF NET PRESENT VALUE OF AFTER TAX NET CASH FLOW ASSOCIATED WITH WOOD OR BARK FUELED SYSTEM
| TOTAL (INCREMENTAL) INITIAL INVESTMENT INCLUDING WORKING CAPITAL | YEAR #3: 215000
| APPROX. NET PRESENT VALUE OF TOTAL INVESTMENTS ALL YEARS | YEAR #3: 215000
e>> | Cost Of Capital to use as "i" in NPV Calculation | YEAR #3: 20%
| PRESENT VALUE OF AT NET CASH FLOW (ATNCF NPV) | YEAR #3: 283411.0043
| SUM OF DEPRECIATION (TOTAL FOR YEARS 1-20) | YEAR #3: 210000
| PRESENT VALUE OF RESIDUAL ASSET SUBJECT TO CAPITAL GAINS TAX (Year 20) | YEAR #3: 438.2121
| PRESENT VALUE OF INITIAL WORKING CAPITAL | YEAR #3: 104.3362
| APPROXIMATE FINAL NPV OF AFTER TAX NET CASH FLOW | YEAR #3: 68953.5526